## Preliminar wiring
Equipment | Electrical components | Installed power | Nominal power[] | Estimated lenght | Rec. Wire
Main supply refrigeration system |  |  | 626.286 |  | To be calculated depending the wire/plate to be used and the distance to transformer room.
1. Compresor pack N250VMD-L (-45ºC) | Compressor motor | 132kW | 98.8 | 25m | 3 wire + ground (section should be calculated by installer)
| Oil pump | 3kW | 3 | 25m | 3 wire + ground (section should be calculated by installer)
| Oil heater with temperature switch | 1kW | 1 | 25m | 3 wire + ground (section should be calculated by installer)
| Low pressure switch | - |  | 25m | 3X1mm2
| High pressure switch | - |  | 25m | 3X1mm2
| Low pressure transducer | - |  | 25m | 2X1mm2 screened
| High pressure transducer | - |  | 25m | 2X1mm2 screened
| Oil pre-filter pressure transducer | - |  | 25m | 2X1mm2 screened
| Oil separator pressure transducer | - |  | 25m | 2X1mm2 screened
| Low temperature transducer | - |  | 25m | 2X1mm2 screened
| High temperature transducer | - |  | 25m | 2X1mm2 screened
| Oil temperature transducer | - |  | 25m | 2X1mm2 screened
| Slide position | - |  | 25m | 4X1mm2 screened
| Capacity 10% feedback | - |  | 25m | 4X1mm2
| Capacity 100% feedback | - |  | 25m
| By-pass solenoid | 14W | 14W | 25m | 3G1mm2
| increase capacity signal | - |  | 25m | 3G1mm2
| decrease capacity signal | - |  | 25m | 3G1mm2
| Oil recovery solenoid | 14W | 14W | 25m | 3G1mm2
2. Compresor pack N200VSD-L (-42ºC) | Compressor motor | 90kW | 42.8 | 25m | 3 wire + ground (section should be calculated by installer)
| Oil pump | 2,2kW | 2.2 | 25m | 3 wire + ground (section should be calculated by installer)
| Oil heater with temperature switch | 1kW | 1 | 25m | 3 wire + ground (section should be calculated by installer)
| Low pressure switch | - |  | 25m | 3X1mm2
| High pressure switch | - |  | 25m | 3X1mm2
| Low pressure transducer | - |  | 25m | 2X1mm2 screened
| High pressure transducer | - |  | 25m | 2X1mm2 screened
| Oil pre-filter pressure transducer | - |  | 25m | 2X1mm2 screened
| Oil separator pressure transducer | - |  | 25m | 2X1mm2 screened
| Low temperature transducer | - |  | 25m | 2X1mm2 screened
| High temperature transducer | - |  | 25m | 2X1mm2 screened
| Oil temperature transducer | - |  | 25m | 2X1mm2 screened
| Slide position | - |  | 25m | 4X1mm2 screened
| Capacity 10% feedback | - |  | 25m | 4X1mm2
| Capacity 100% feedback | - |  | 25m
| By-pass solenoid | 14W | 14W | 25m | 3G1mm2
| increase capacity signal | - |  | 25m | 3G1mm2
| decrease capacity signal | - |  | 25m | 3G1mm2
| Oil recovery solenoid | 14W | 14W | 25m | 3G1mm2
3. Compresor pack N200VMD-L (-12ºC) | Compressor motor | 200kW | 174 | 25m | 3 wire + ground (section should be calculated by installer)
| Oil pump | 5kW | 5 | 25m | 3 wire + ground (section should be calculated by installer)
| Oil heater with temperature switch | 1kW | 1 | 25m | 3 wire + ground (section should be calculated by installer)
| Low pressure switch | - |  | 25m | 3X1mm2
| High pressure switch | - |  | 25m | 3X1mm2
| Low pressure transducer | - |  | 25m | 2X1mm2 screened
| High pressure transducer | - |  | 25m | 2X1mm2 screened
| Oil pre-filter pressure transducer | - |  | 25m | 2X1mm2 screened
| Oil separator pressure transducer | - |  | 25m | 2X1mm2 screened
| Low temperature transducer | - |  | 25m | 2X1mm2 screened
| High temperature transducer | - |  | 25m | 2X1mm2 screened
| Oil temperature transducer | - |  | 25m | 2X1mm2 screened
| Slide position | - |  | 25m | 4X1mm2 screened
| Capacity 10% feedback | - |  | 25m | 4X1mm2
| Capacity 100% feedback | - |  | 25m
| By-pass solenoid | 14W | 14W | 25m | 3G1mm2
| increase capacity signal | - |  | 25m | 3G1mm2
| decrease capacity signal | - |  | 25m | 3G1mm2
| Oil recovery solenoid | 14W | 14W | 25m | 3G1mm2
4. Compresor pack N200VMD-L (-12ºC) | Compressor motor | 200kW | 174 | 25m | 3 wire + ground (section should be calculated by installer)
| Oil pump | 5kW | 5 | 25m | 3 wire + ground (section should be calculated by installer)
| Oil heater with temperature switch | 1kW | 1 | 25m | 3 wire + ground (section should be calculated by installer)
| Low pressure switch | - |  | 25m | 3X1mm2
| High pressure switch | - |  | 25m | 3X1mm2
| Low pressure transducer | - |  | 25m | 2X1mm2 screened
| High pressure transducer | - |  | 25m | 2X1mm2 screened
| Oil pre-filter pressure transducer | - |  | 25m | 2X1mm2 screened
| Oil separator pressure transducer | - |  | 25m | 2X1mm2 screened
| Low temperature transducer | - |  | 25m | 2X1mm2 screened
| High temperature transducer | - |  | 25m | 2X1mm2 screened
| Oil temperature transducer | - |  | 25m | 2X1mm2 screened
| Slide position | - |  | 25m | 4X1mm2 screened
| Capacity 10% feedback | - |  | 25m | 4X1mm2
| Capacity 100% feedback | - |  | 25m
| By-pass solenoid | 14W | 14W | 25m | 3G1mm2
| increase capacity signal | - |  | 25m | 3G1mm2
| decrease capacity signal | - |  | 25m | 3G1mm2
| Oil recovery solenoid | 14W | 14W | 25m | 3G1mm2
5. Evaporative condenser | Fan n1 | 11kW | 8.9 | 40m | 3 wire + ground (section should be calculated by installer)
| Fan n2 | 11kW | 8.9 | 40m | 3 wire + ground (section should be calculated by installer)
| Fan n3 | 11kW | 8.9 | 40m | 3 wire + ground (section should be calculated by installer)
| Water pump | 3kW | 3 | 40m | 3 wire + ground (section should be calculated by installer)
| Heater for low temperatures | 3kW | 3 | 40m | 3 wire + ground (section should be calculated by installer)
| Drainage solenoid valve | 40W | 40W | 40m | 3G1mm2
| Ambient temperature sensor | - |  | 40m | 4X1mm2 screened
6. Warm glycol cooler | Fan n1 | 2,2kW | 1.9 | 40m | 3 wire + ground (section should be calculated by installer)
| Fan n2 | 2,2kW | 1.9 | 40m
| Fan n3 | 2,2kW | 1.9 | 40m
| Fan n4 | 2,2kW | 1.9 | 40m
| Fan n5 | 2,2kW | 1.9 | 40m
| Fan n6 | 2,2kW | 1.9 | 40m
Surge drum -45ºC | Pump n1 | 4kW | 4 | 25m | 3 wire + ground (section should be calculated by installer)
| Pump n2 | 4kW | 4 | 25m | 3 wire + ground (section should be calculated by installer)
| Level switch (working point) | - |  | 25m | 3x1mm2
| Level switch (minimum) | - |  | 25m | 3x1mm2
| Level transducer | - |  | 25m | 4x1mm2 screened
| Temperature pump n1 | - |  | 25m | 2X1mm2 screened
| Temperature pump n2 | - |  | 25m | 2X1mm2 screened
| Solenoid liquid injection | - |  | 25m | 3G1mm2
| Electronic expansion valve | - |  | 25m | 5x1mm2 screened
| Surge drum pressure |  |  | 25m | 2X1mm2 screened
| Pumps discharge pressure |  |  | 25m | 2X1mm2 screened
Surge drum -42ºC | Pump n1 | 4kW | 4 | 25m | 3 wire + ground (section should be calculated by installer)
| Pump n2 | 4kW | 4 | 25m | 3 wire + ground (section should be calculated by installer)
| Level switch (working point) | - |  | 25m | 3x1mm2
| Level switch (minimum) | - |  | 25m | 3x1mm2
| Level transducer | - |  | 25m | 4x1mm2 screened
| Temperature pump n1 | - |  | 25m | 2X1mm2 screened
| Temperature pump n2 | - |  | 25m | 2X1mm2 screened
| Solenoid liquid injection | - |  | 25m | 3G1mm2
| Electronic expansion valve | - |  | 25m | 5x1mm2 screened
| Surge drum pressure |  |  | 25m | 2X1mm2 screened
| Pumps discharge pressure |  |  | 25m | 2X1mm2 screened
Surge drum -12ºC | Pump n1 | 4kW | 4 | 25m | 3 wire + ground (section should be calculated by installer)
| Pump n2 | 4kW | 4 | 25m | 3 wire + ground (section should be calculated by installer)
| Level switch (working point) | - |  | 25m | 3x1mm2
| Level switch (minimum) | - |  | 25m | 3x1mm2
| Level transducer | - |  | 25m | 4x1mm2 screened
| Temperature pump n1 | - |  | 25m | 2X1mm2 screened
| Temperature pump n2 | - |  | 25m | 2X1mm2 screened
| Solenoid liquid injection | - |  | 25m | 3G1mm2
| Electronic expansion valve | - |  | 25m | 5x1mm2 screened
| Surge drum pressure |  |  | 25m | 2X1mm2 screened
| Pumps discharge pressure |  |  | 25m | 2X1mm2 screened
Glycol pumping station | Cold glicol pump n1 | 30kW | 8 | 20m | 3 wire + ground (section should be calculated by installer)
| Cold glicol pump n2 | 30kW | 8 | 20m | 3 wire + ground (section should be calculated by installer)
| Cold glicol pump n3 | 30kW | 8 | 20m | 3 wire + ground (section should be calculated by installer)
| Warm glycol pump n1 | 30kW | 8 | 20m | 3 wire + ground (section should be calculated by installer)
| Warm glicol pump n2 | 30kW | 8 | 20m | 3 wire + ground (section should be calculated by installer)
| Temperature cold pump n1 | - |  | 20m | 2X1mm2 screened
| Temperature cold pump n2 | - |  | 20m | 2X1mm2 screened
| Temperature cold pump n3 | - |  | 20m | 2X1mm2 screened
| Temperature warm pump n1 | - |  | 20m | 2X1mm2 screened
| Temperature warm pump n2 | - |  | 20m | 2X1mm2 screened
| Temperature warm vessel | - |  | 20m | 4x1mm2 screened
| Temperature cold vessel | - |  | 20m | 4x1mm2 screened
| Temperature impulsion cold glycol | - |  | 20m | 4x1mm2 screened
| Temperature impulsion warm glycol | - |  | 20m | 4x1mm2 screened
| Flow switch cold glycol exchanger | - |  | 20m | 4x1mm2 screened
| Flow switch warm glycol exchanger | - |  | 20m | 4x1mm2 screened
| Low level switch cold glycol vessel | - |  | 20m | 3x1mm2
| Low level switch warm glycol vessel | - |  | 20m | 3x1mm2
| Level transducer expansion vessel cold glycol | - |  | 20m | 4x1mm2 screened
| Level transducer expansion vessel warm glycol | - |  | 20m | 4x1mm2 screened
| Dry cooler inlet temperature | - |  | 20m | 4x1mm2 screened
| Dry cooler outlet temperature | - |  | 20m | 4x1mm2 screened
| Three way valve Dry cooler | 100W | 100W | 20m | 5x1mm2 screened
Discharge line | Discharge pressure |  |  | 25m | 2X1mm2 screened
| Hot gas motorized valve |  |  | 25m | 4x1mm2 screened
Frozen cold storage evaporator n1 | Fan n1 | 0,62kW | 0.54 | 30m | 3 wire + ground (section should be calculated by installer)
| Fan n2 | 0,62kW | 0.54 | 30m
| Fan n3 | 0,62kW | 0.54 | 30m
| Fan n4 | 0,62kW | 0.54 | 30m
| Drainage hose heater | 300W | 0.3 | 30m | 3G1,5mm2
| Liquid injection solenoid | 14W | 14W | 30m | 3G1mm2
| Hot gas injection solenoid | 14W | 14W | 30m | 3G1mm2
| Coil temperature for defrost | - |  | 30m | 2X1mm2 screened
| Suction motorized valve | 100W | 100W | 30m | 4x1mm2 screened
Frozen cold storage evaporator n2 | Fan n1 | 0,62kW | 0.54 | 35m | 3 wire + ground (section should be calculated by installer)
| Fan n2 | 0,62kW | 0.54 | 35m
| Fan n3 | 0,62kW | 0.54 | 35m
| Fan n4 | 0,62kW | 0.54 | 35m
| Drainage hose heater | 300W | 0.3 | 35m | 3G1,5mm2
| Liquid injection solenoid | 14W | 14W | 35m | 3G1mm2
| Hot gas injection solenoid | 14W | 14W | 35m | 3G1mm2
| Coil temperature for defrost |  |  | 35m | 2X1mm2 screened
| Suction motorized valve | 100W | 100W | 35m | 4x1mm2 screened
Temperature cold storage | Temperature cold storage |  |  | 30m | 4x1mm2 screened
Smoking fillet storage evaporator n1 | Fan n1 | 2,85kW | 2.82 | 180m | 3 wire + ground (section should be calculated by installer)
| Drainage hose heater | 300W | 0.3 | 180m | 3G1,5mm2
| Liquid injection solenoid | 14W | 14W | 180m | 3G1mm2
| Hot gas injection solenoid | 14W | 14W | 180m | 3G1mm2
| Coil temperature for defrost |  |  | 180m | 2x1mm2 screened
| Suction motorized valve | 100W | 100W | 180m | 4x1mm2 screened
Smoking fillet storage evaporator n2 | Fan n1 | 2,85kW | 2.82 | 180m | 3 wire + ground (section should be calculated by installer)
| Drainage hose heater | 300W | 0.3 | 180m | 3G1,5mm2
| Liquid injection solenoid | 14W | 14W | 180m | 3G1mm2
| Hot gas injection solenoid | 14W | 14W | 180m | 3G1mm2
| Coil temperature for defrost |  |  | 180m | 2x1mm2 screened
| Suction motorized valve | 100W | 100W | 180m | 4x1mm2 screened
Temperature Smoking fillet storage | Temperature cold storage |  |  | 180m | 4x1mm2 screened
Blast freezer evaporator | Fan n1 | 3,6kW | 3.6 | 180m | 3 wire + ground (section should be calculated by installer)
| Fan n2 | 3,6kW | 3.6 | 180m
| Fan n3 | 3,6kW | 3.6 | 180m
| Fan ring heaters | 150W | 0.15 | 180m | 3G1,5mm2
| Drainage hose heater | 300W | 0.3 | 180m | 3G1,5mm2
| Liquid injection solenoid | 14W | 14W | 180m | 3G1mm2
| Hot gas injection solenoid | 14W | 14W | 180m | 3G1mm2
| Coil temperature for defrost |  |  | 180m | 2x1mm2 screened
| Suction motorized valve | 100W | 100W | 180m | 4x1mm2 screened
| Blast freezer temperature |  |  | 180m | 4x1mm2 screened
Air cooler with warm glycol for dehumidifing IQF room n1 | Fan n1 | 350W | 0.32 | 110m | 3 wire + ground (section should be calculated by installer)
| Fan n2 | 350W | 0.32 | 110m
| Fan n3 | 350W | 0.32 | 110m
| Cold glycol solenoid | 40W | 40W | 110m | 3G1mm2
| Warm glycol solenoid | 40W | 40W | 110m | 3G1mm2
Air cooler with warm glycol for dehumidifing IQF room n2 | Fan n1 | 350W | 0.32 | 100m | 3 wire + ground (section should be calculated by installer)
| Fan n2 | 350W | 0.32 | 100m
| Fan n3 | 350W | 0.32 | 100m
| Cold glycol solenoid | 40W | 40W | 100m | 3G1mm2
| Warm glycol solenoid | 40W | 40W | 100m | 3G1mm2
Clima IQF | Room temperature |  |  | 105m | 4x1mm2 screened
| Room humidity |  |  | 105m | 3x1mm2 screened
Air cooler with warm glycol for dehumidifing slicing room n1 | Fan n1 | 350W | 0.32 | 170m | 3 wire + ground (section should be calculated by installer)
| Fan n2 | 350W | 0.32 | 170m
| Fan n3 | 350W | 0.32 | 170m
| Cold glycol solenoid | 40W | 40W | 170m | 3G1mm2
| Warm glycol solenoid | 40W | 40W | 170m | 3G1mm2
Air cooler with warm glycol for dehumidifing slicing room n2 | Fan n1 | 350W | 0.32 | 150m | 3 wire + ground (section should be calculated by installer)
| Fan n2 | 350W | 0.32 | 150m
| Fan n3 | 350W | 0.32 | 150m
| Cold glycol solenoid | 40W | 40W | 150m | 3G1mm2
| Warm glycol solenoid | 40W | 40W | 150m | 3G1mm2
Clima slicing room | Room temperature |  |  | 150m | 4x1mm2 screened
| Room humidity |  |  | 150m | 3x1mm2 screened
Air cooler with warm glycol for dehumidifing main storage cartoons | Fan n1 | 175W | 0.15 | 150m | 3 wire + ground (section should be calculated by installer)
| Fan n2 | 175W | 0.15 | 150m
| Fan n3 | 175W | 0.15 | 150m
| Cold glycol solenoid | 40W | 40W | 150m | 3G1mm2
| Warm glycol solenoid | 40W | 40W | 150m | 3G1mm2
Clima slicing room | Room temperature |  |  | 150m | 4x1mm2 screened
| Room humidity |  |  | 150m | 3x1mm2 screened
Product storage air cooler n1 | Fan | 2,06kW | 1.689 | 35m | 3 wire + ground (section should be calculated by installer)
| Solenoid glycol inlet | 40W | 40W | 35m | 3G1mm2
| Defrost heaters | 1kW | 1 | 35m | 2 wire + ground (section should be calculated by installer)
| Coil temperature for defrost | - |  | 35m | 2x1mm2 screened
Product storage air cooler n2 | Fan | 2,06kW | 1.689 | 45m | 3 wire + ground (section should be calculated by installer)
| Solenoid glycol inlet | 40W | 40W | 45m | 3G1mm2
| Defrost heaters | 1kW | 1 | 45m | 2 wire + ground (section should be calculated by installer)
| Coil temperature for defrost | - |  | 45m | 2x1mm2 screened
Temperature product storage room | room temperature | - |  | 40m | 4x1mm2 screened
Raw material storage air cooler n1 | Fan | 2,06kW | 1.689 | 50m | 3 wire + ground (section should be calculated by installer)
| Solenoid glycol inlet | 40W | 40W | 50m | 3G1mm2
| Defrost heaters | 1kW | 1 | 50m | 2 wire + ground (section should be calculated by installer)
| Coil temperature for defrost | - |  | 50m | 2x1mm2 screened
Raw material storage air cooler n2 | Fan | 2,06kW | 1.689 | 60m | 3 wire + ground (section should be calculated by installer)
| Solenoid glycol inlet | 40W | 40W | 60m | 3G1mm2
| Defrost heaters | 1kW | 1 | 60m | 2 wire + ground (section should be calculated by installer)
| Coil temperature for defrost | - |  | 60m | 2x1mm2 screened
Temperature raw material storage room | room temperature | - |  | 55m | 4x1mm2 screened
Room nº1 air cooler | Fan | 1,28kW | 1 | 110m | 3 wire + ground (section should be calculated by installer)
| Solenoid glycol inlet | 40W | 40W | 110m | 3G1mm2
| Defrost heaters | 1kW | 1 | 110m | 2 wire + ground (section should be calculated by installer)
| Coil temperature for defrost | - |  | 110m | 2x1mm2 screened
Room nº1 temperature | room temperature | - |  | 110m | 4x1mm2 screened
Room nº7 air cooler | Fan | 1,28kW | 1 | 115m | 3 wire + ground (section should be calculated by installer)
| Solenoid glycol inlet | 40W | 40W | 115m | 3G1mm2
| Defrost heaters | 1kW | 1 | 115m | 2 wire + ground (section should be calculated by installer)
| Coil temperature for defrost | - |  | 115m | 2x1mm2 screened
Room nº7 temperature | room temperature | - |  | 115m | 4x1mm2 screened
Room nº2 air cooler n1 | Fan | 1,28kW | 1 | 160m | 3 wire + ground (section should be calculated by installer)
| Solenoid glycol inlet | 40W | 40W | 160m | 3G1mm2
Room nº2 air cooler n1 | Fan | 1,28kW | 1 | 160m | 3 wire + ground (section should be calculated by installer)
| Solenoid glycol inlet | 40W | 40W | 160m | 3G1mm2
Room nº2 temperature | room temperature | - |  | 160m | 4x1mm2 screened
Room nº4 air cooler | Fan | 520W | 0.44 | 125m | 3 wire + ground (section should be calculated by installer)
| Solenoid glycol inlet | 40W | 40W | 125m | 3G1mm2
Room nº4 temperature | room temperature | - |  | 125m | 4x1mm2 screened
Room nº17 air cooler | Fan | 520W | 0.44 | 110m | 3 wire + ground (section should be calculated by installer)
| Solenoid glycol inlet | 40W | 40W | 110m | 3G1mm2
Room nº17 temperature | room temperature | - |  | 110m | 4x1mm2 screened
Ammonia security system | Exhaust fan machinery room | 7,5kW | 7.5 | 25m | 3 wire + ground (section should be calculated by installer)
| Ammonia leakage central with sensor | - |  | 20m | 6 wires + ground x 1mm2
Rapid air purger | Rapid air purger | 10kW | 3.5 | 25m | 2wire + ground
| Solenoid purgue point 1 | 14W | 14W | 25m | 3G1mm2
| Solenoid purge point 2 | 14W | 14W | 25m | 3G1mm2
| Solenoid purgue point 3 | 14W | 14W | 25m | 3G1mm2