# Annex No. 2

TECHNICAL SPECIFICATION

PURCHASE OF DRIVE-THRU BLAST CHILLER (2-TROLLEY, ROLL-IN TYPE)

place, date

| Parameter | Requirement |
| --- | --- |
| THE PARTICIPANT shall provide information or proof against each requirement. |  |
| Quantity | 3 pcs. – Industrial drive-thru blast chiller (roll-in type) for rapid chilling/freezing of cooked food on trolleys. |
| Brand, model offered | Brand name (for identification purposes) and model name (for identification purposes). |
| Purpose | Blast chiller must perform rapid cooling and freezing cycles in CPU (central production unit) environment. Suitable for hot → cold workflows, chilling cooked food from +90°C to +3°C within ≤ 90 minutes, and from +90°C to –18°C within cycle parameters defined by manufacturer. |
| Blast chilling / freezing performance | System must support: |
|  | • positive cycle: +90°C → +3°C in ≤ 90 min for load within 400–500 kg (per cycle), |
|  | • negative cycle: +90°C → –18°C in manufacturer-specified time for min. 300 kg load. |
|  | Performance data must be manufacturer-certified. |
| Trolley capacity | Unit must accept 2 roll-in trolleys of GN 1/1 or EN 600×400 format. Internal chamber shall accommodate at least 2 full-size trolleys simultaneously (roll-in). |
| Overall dimensions (L × W × H) | External dimensions must be within: |
|  | • length 2100–2300 mm, |
|  | • width 2200–2400 mm, |
|  | • height 2350–2550 mm. |
| Internal dimensions | Internal chamber shall allow safe manoeuvring of two GN1/1 trolleys: minimum internal width 750 mm, internal depth 4000–4400 mm, internal height 1800–2000 mm. |
| Construction and materials | Monoblock structure from stainless steel minimum AISI 304, external finish satin/scotch-brite acceptable. All internal corners must be rounded. Insulation thickness not less than 100 mm, using high-density polyurethane foam (min. 40 kg/m³). |
| Doors (drive-thru double-door) | Must include double-door drive-thru configuration (hot side → cold side). Both doors insulated, with removable magnetic gaskets and door micro-switches that stop fans when doors are open. |
| Refrigerant | Natural or low-GWP refrigerant. Acceptable range: R290, R452A or equivalent EU-compliant refrigerant with GWP in line with F-gas regulation. |
| Cooling system | Air-cooled or water-cooled remote condensing unit. Remote motor capacity must be suitable for declared chilling/freezing loads: 6.5–8.0 kW total power input per chiller (or equivalent freezer-class capacity). Supplier must specify capacity. |
| Power supply | 400V 3~ 50Hz (or 400V 3+N 50Hz), compatible with EU industrial installations. |
| Airflow system | Frontal or multi-directional air circulation ensuring uniform temperature distribution across 2 trolleys. Airflow must prevent surface icing and ensure even penetration of cold air. |
| Core probe | Must include heated core probe (factory standard) with temperature logging function. |
| HACCP data logging | Integrated HACCP-compliant logging system: must record time, temperature curves (product and air), cycle parameters, alarms. USB export or equivalent digital export required. |
| Control panel | Digital control panel with programmable cycles (positive, negative, holding), temperature display, alarms, probe management and logging. |
| Safety features | Emergency switches, door micro-switches, overload protection, and compliance with EU industrial safety requirements. |
| Cleaning and hygiene | Internal chamber must allow full cleaning access; evaporator must be easily accessible. Condensate drainage system must be integrated. |
| Installation requirements | Unit must be delivered fully assembled (monoblock) except for connection to power and refrigerant piping (if remote motor). No structural assembly on site is permitted. |
| Complete functional set (mandatory) | The following must be included in the offered price: |
|  | • blast chiller monoblock unit |
|  | • 2-trolley internal chamber |
|  | • drive-thru double doors |
|  | • heated core probe |
|  | • HACCP logging system |
|  | • remote condensing unit (air-cooled or water-cooled) |
|  | • all necessary sensors, fans, evaporator |
|  | • anchoring feet or base frame |
|  | • any required accessories for full operation |
| THE PARTICIPANT must provide a full list of included components. |  |
| Documentation | To be supplied in Latvian or English: user manual, technical passport, HACCP logging instructions, electric diagram, maintenance instructions, declaration of conformity. |
| Compliance and CE marking | Equipment must comply with EU Machinery Directive, EMC, LVD and refrigerant-related legislation. CE marking mandatory. |
| Guarantee | Minimum 24 months full manufacturer or supplier warranty. |

Name, surname, position

signature