## Annex No. 2

## Technical Specification

### Purchase of Industrial Water Chiller for Dough Production

| Parameter | Requirement |
| --- | --- |
| THE PARTICIPANT shall provide information or proof against each requirement. |  |
| Quantity | 1 pc. – Industrial Water Chiller unit for cooling water used in dough mixing. |
| Purpose | To supply chilled water at a precise and controlled temperature to dough mixers (impastatrici) and other bakery equipment, thereby enabling precise control over dough temperature during mixing cycles, essential for yeast and enzyme activity. |
| Performance Specifications |  |
| * Cooling Capacity (Output) | Must be capable of cooling/producing a minimum of 500 L – 550 L of cold water per hour. |
| * Water Output Temperature | Capable of reaching and maintaining a minimum temperature of +C – +2C. |
| * Refrigeration System | Forced ventilation/air-cooled condensation unit. |
| * Pump System | Built-in water recirculation pump system (or dedicated external pump specified in the offer). |
| * Tank Capacity | Insulated stainless steel storage tank capacity: 180 L – 220 L. |
| Refrigeration Circuit |  |
| * Refrigerant Type | Environmentally friendly refrigerant with low GWP (e.g., R452a, R448A, R513A, or equivalent approved HFC/HFO blend). |
| * Temperature Control | Electronic temperature control panel allowing precise setting and monitoring of water output temperature. |
| Technical & Energy |  |
| * Power Supply | 400V / 3N PE / 50 Hz (Three-phase industrial standard). |
| * Maximum Connected Load | 3.0 kW – 3.5 kW. |
| * Weight | 180 kg – 200 kg. |
| Construction & Mobility |  |
| * Material | External panels and water tank made of Stainless Steel (AISI 304 or equivalent). |
| * Installation | Mounted on wheels (castors) for mobility. |
| Complete Functional Set (Mandatory) | The Supplier must ensure the delivery of a fully integrated and functional chiller unit, ready for immediate connection to the water supply and dough mixers. The offer must explicitly include: |
|  | • The complete refrigeration circuit and insulated storage tank. |
|  | • All necessary internal pumps, valves, sensors, and connecting materials for standard installation. |
|  | • Commissioning and comprehensive staff training. |
| Documentation | To be supplied in Latvian or English: user manual, electric diagram, maintenance instructions, and CE Declaration of Conformity. |
| Compliance | Equipment must comply with relevant EU directives (e.g., Machinery Directive 2006/42/EC). CE marking is mandatory. |
| Guarantee | Minimum 24 months full manufacturer or supplier warranty. |