Annex No. 2
Technical Specification
Purchase of Industrial Waste Disposal Coolers 
	Parameter
	Requirement

	THE PARTICIPANT shall provide information or proof against each requirement.
	

	Quantity
	4 pcs. – Industrial Waste Disposal Coolers (Waste Bin Cooling Cabinets).

	Purpose
	To hygienically cool and store food waste, preventing bacterial growth and minimizing odors by maintaining controlled low temperatures. Designed for accepting and cooling two standard large-volume waste bins.

	1. Capacity and Dimensions
	

	* Waste Bin Capacity
	Designed to accommodate two (2) waste bins of 240 Litres each.

	* Total Gross Capacity
	1100 Litres – 1150 Litres.

	* External Length (L)
	1700 mm – 1720 mm.

	* External Depth (D)
	860 mm – 880 mm.

	* External Height (H)
	1190 mm – 1210 mm.

	2. Temperature and Cooling System (Self-Contained)
	

	* Working Temperature Range
	+2C to +15C.

	* Ambient Operation
	Suitable for ambient temperatures ranging from +15C to +40C.

	* Refrigeration Unit
	Integrated, self-contained refrigerating unit (Built-in cooling).

	* Refrigerant Type
	R290 (Hydrocarbon, low GWP).

	* Defrost System
	Automatic defrosting and evaporation of defrost water using hot gas.

	3. Construction and Technical Requirements
	

	* Material
	Constructed from Stainless Steel.

	* Evaporator
	Evaporator system must be foamed-in (e.g., in the stainless steel back wall).

	* Access
	Equipped with a hinged poor-in aperture (lid) for waste disposal access.

	* Controls
	Must feature electronic control.

	* Power / Load
	Connected load: 350 W – 450 W.

	* Electrical Supply
	230 V, 50 Hz.

	Complete Functional Set (Mandatory)
	The Supplier must ensure the delivery of four fully functional Waste Disposal Cooler units, complete, assembled, and ready to plug in. The offer must explicitly include: the cooler unit, integrated refrigerating unit, all internal components, and the automatic defrost/evaporation system.

	Documentation
	To be supplied in Latvian or English: user manual, electric diagram, maintenance instructions, and CE Declaration of Conformity.

	Guarantee
	Minimum 24 months full manufacturer or supplier warranty.



